## Sheet1
Design Flows | MGD | ML/D |  |  | Design parameters
Conventional Effluent | 70 | 264.6 |  |  | lifetime | 40 | years
| 264.6 |  |  |  | discount rate | 4 | percent
RO concentrate for O3 and BAC | 10.5 | 39.69 |  |  | annuity factor first term | 0.20829 | https://www.investopedia.com/terms/e/eac.asp
MF unit | 70 | 264.6 |  |  | annuity factor | 19.7928
RO unit | 70 | 264.6
AOP | 59.5 | 224.91
BAC units | RO Concentrate Treatment | [7 empty] | Conventional Effluent Treatment
10 min EBCT
Capital cost ($M/MGD) | 0.96357 | 2011 dollars | [6 empty] | 0.70193 | 2011 dollars
capital cost ($M) | 10.1175 | 2011 dollars | [6 empty] | 49.135 | 2011 dollars
O+M cost ($M/MGD/yr) | 0.053111 | 2011 dollars | [6 empty] | 0.048857 | 2011 dollars
O+M cost ($M/yr) | 0.55766 | 2011 dollars | [6 empty] | 3.42 | 2011 dollars
20 min EBCT
Capital cost ($M/MGD) | 1.0758 | 2011 dollars | [6 empty] | 0.81398 | 2011 dollars
capital cost ($M) | 11.2958 | 2011 dollars | [6 empty] | 56.9787 | 2011 dollars
O+M cost ($M/MGD/yr) | 0.06147 | 2011 dollars | [6 empty] | 0.057412 | 2011 dollars
O+M cost ($M/yr) | 0.64544 | 2011 dollars | [6 empty] | 4.0188 | 2011 dollars
30 min EBCT |  | assume the sum for the 10 min and 20 min EBCTs in series
capital cost ($M) | 21.4134 | 2011 dollars | [6 empty] | 106.1136 | 2011 dollars
capital cost ($M) | 25.9905 | adjusted to July 2019 dollars using RSMeans | [6 empty] | 128.7954 | adjusted to July 2019 dollars using RSMeans
O+M cost ($M/yr) | 1.2031 | 2011 dollars | [6 empty] | 7.4389 | 2011 dollars
O+M cost ($M/yr) | 1.4603 | adjusted to July 2019 dollars using RSMeans | [6 empty] | 9.0289 | adjusted to July 2019 dollars using RSMeans
Equivalent annual cost (EAC in $M/yr) | 3.6761 | [7 empty] | 16.4389
Footprint (ft2) | 1740 | From Plumlee et al (2014) for 10 min or 20 min EBCT BAC units at ~10 MGD | [6 empty] | 12153 | From Plumlee et al (2014) for 10 min or 20 min EBCT BAC units at 70 MGD
footprint (m2) | 161.7341 | m2 | [6 empty] | 1129.6289 | m2
Methanol needed for denitifying biofilters, which is same needed for BAC units
Nitrate conc (mg-N/L) in conventional effluent | 10.4478
methanol cost paris - euro/1000 m3 for 26 mg_N/L nitrogen | 15
methanol cost paris - euro/1000 m3 for 10.5 mg_N/L nitrogen | 6.0276 | based on proportion for levels of nitrate in conventional study vs. Parisian study (Rocher et al., 2012)
gallons per year treated | 25550000000 | for 70 MGD nitrified effluent into denitrified biofilter
m3/yr treated | 96579000
1000 m3/yr treated | 96579
euros/yr | 582135.1894
dol/yr in 2012 | 756775.7463 | based on $1.3/euro in 2012
dol/yr in 2017 | 902738.6359 | adjusted to July 2019 dollars using RSMeans
total ($M/yr) | 0.90274
O3 treatment of concentrate | RO Concentrate Treatment | [7 empty] | Conventional Effluent Treatment
Capital cost ($M/MGD) | 0.63484 | 2011 dollars | [6 empty] | 0.22791 | 2011 dollars
capital cost ($M) | 6.6658 | 2011 dollars | [6 empty] | 15.9534 | 2011 dollars
delta capital cost for higher O3 dose ($M) | 0.9828 | 2011 dollars and 20 mg/L dose | [6 empty] | 0 | 2011 dollars and 20 mg/L dose
total cap cost ($M) | 7.6486 | 2011 dollars | [6 empty] | 15.9534 | 2011 dollars
total cap cost ($M) | 9.2835 | adjusted to July 2019 dollars using RSMeans | [6 empty] | 19.3635 | adjusted to July 2019 dollars using RSMeans
O+M cost ($M/MGD/yr) | 0.0060301 | 2011 dollars without correction for higher O3 dose | [6 empty] | 0.005473 | 2011 dollars without correction for higher O3 dose
O+M cost ($M/yr) | 0.063316 | 2011 dollars without correction for higher O3 dose | [6 empty] | 0.38311 | 2011 dollars without correction for higher O3 dose
delta O+M cost for higher O3 dose ($M/yr) | 0.315 | 2011 dollars | [6 empty] | 0
total O+M cost ($M/yr) | 0.37832 | 2011 dollars | [6 empty] | 0.38311 | 2011 dollars
total O+M cost ($M/yr) | 0.45918 | adjusted to July 2019 dollars using RSMeans | [6 empty] | 0.465 | adjusted to July 2019 dollars using RSMeans
Footprint for ozone
height (ft) | 10 | assumed | [6 empty] | 10 | assumed
hydraulic residence time (min) | 10 | assumed | [6 empty] | 10 | assumed
hydraulic residence time (d) | 0.0069444 | d | [6 empty] | 0.0069444 | d
volume for 10.5 MGD | 0.072917 | MG | [6 empty] | 0.48611 | MG
volume for 10.5 MGD | 72916.6667 | gal | [5 empty] | volume for 70 MGD | 486111.1111 | gal
volume for 10.5 MGD | 9748.9583 | ft3 | [5 empty] | volume for 70 MGD | 64993.0556 | ft3
footprint | 974.8958 | ft2 | O3 only |  |  |  |  | footprint | 6499.3056 | ft2 | O3 only
footprint | 90.6172 | m2 | O3 only |  |  |  |  | footprint | 604.1145 | m2 | O3 only
O3/BAC treatment
capital cost ($M) | 35.274 | adjusted to July 2019 dollars using RSMeans | [6 empty] | 148.1589 | adjusted to July 2019 dollars using RSMeans
O+M cost ($M/yr) | 1.9194 | adjusted to July 2019 dollars using RSMeans | [6 empty] | 9.4939 | adjusted to July 2019 dollars using RSMeans
EAC ($M/yr) | 4.6043 | [7 empty] | 17.8822
| 0.92822 | [7 empty] | 1.4433
Total footprint | 252.3513 | m2 | [6 empty] | 1733.7435 | m2
MF/RO/AOP treatment train
MF capital cost ($M/MGD) | 1.3835 | 2011 dollars
MF capital cost ($M) | 96.8425 | 2011 dollars
MF O+M cost ($M/MGD/yr) | 0.1195 | 2011 dollars
MF O+M cost ($M/yr) | 8.365 | 2011 dollars
RO capital cost ($M/MGD) | 2.7669 | 2011 dollars
RO capital cost ($M) | 193.685 | 2011 dollars
RO O+M cost ($M/MGD/yr) | 0.24722 | 2011 dollars
RO O+M cost ($M/yr) | 17.3057 | 2011 dollars
AOP capital cost ($M/MGD) | 0.37706 | 2011 dollars
AOP capital cost ($M) | 22.4348 | 2011 dollars
AOP O+M cost ($M/MGD/yr) | 0.030726 | 2011 dollars
AOP O+M cost ($M/yr) | 1.8282 | 2011 dollars
MF/RO/AOP capital cost ($M) | 312.9623 | 2011 dollars
MF/RO/AOP capital cost ($M) | 379.858 | adjusted to July 2019 dollars using RSMeans
MF/RO/AOP O+M cost ($M/yr) | 27.4989 | 2011 dollars
MF/RO/AOP O+M cost ($M/yr) | 33.3768 | adjusted to July 2019 dollars using RSMeans
EAC ($M/yr) | 52.5685
| OCWD |  | MGD reuse facility
Footprint | flow | ft2 | ft2 | m2
MF | 117.6471 | 18000 | 10710
RO | 117.6471 | 23500 | 13982.5
AOP | 100 | 2500 | 1487.5
total |  |  | 26180 | 2433.4474