Table1.The water quality indexes of SG-FBF in 9 mining well

|  | Well no. | Na+ mg.L-1 | Ca2+ mg.L-1 | Mg2+ mg.L-1 | Fe mg.L-1 | Cl- mg.L-1 | HCO3- mg.L-1 | SO42- mg.L-1 | TDS mg.L-1 | CODCr mg.L-1 | BOD5 mg.L-1 | NH3-N mg.L-1 | TN mg.L-1 | SS mg.L-1 | pH |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Early period | 102 | 1621.67 | 11.02 | 2.43 | 0.00 | 4874.38 | 646.81 | 500 | 7656.31 | 2356.24 | 135.00 | 37.40 | 39.80 | 314.00 | 7.50 |
|  | 1 | 2856.45 | 66.13 | 15.80 | 1.00 | 3899.50 | 390.53 | 500 | 7728.41 | 2326.00 | 105.00 | 27.10 | 38.80 | 211.00 | 7.00 |
|  | 102H1-1 | 3746.87 | 128.26 | 35.25 | 6.00 | 5583.38 | 97.63 | 500 | 10091.38 | 1334.95 | 95.00 | 28.80 | 39.10 | 345.00 | 7.00 |
|  | 105 | 4401.97 | 156.31 | 59.56 | 3.00 | 6292.38 | 720.04 | 500 | 12130.25 | 479.83 | 32.00 | 13.30 | 23.30 | 422.00 | 7.00 |
|  | 103 | 4437.69 | 160.00 | 24.00 | 20.00 | 6833.75 | 671.88 | 24 | 12151.32 | 471.00 | 21.00 | 35.10 | 38.90 | 332.00 | 6.88 |
|  | 102H1-5 | 2859.11 | 95.19 | 15.19 | 5.00 | 4147.65 | 748.23 | 72.05 | 7937.41 | 2238.34 | 110.00 | 32.50 | 37.90 | 340.00 | 6.53 |
|  | 102H1-4 | 1059.23 | 30.06 | 9.11 | 3.00 | 1134.40 | 992.55 | 12.01 | 3237.36 | 4209.58 | 170.00 | 25.80 | 35.80 | 407.00 | 7.14 |
|  | 105H1-2 | 145.98 | 2.97 | 62.12 | 5.00 | 12.45 | 106.35 | 0.00 | 329.87 | 5429.00 | 210.00 | 36.00 | 39.90 | 410.00 | 6.30 |
|  | 108H1-1 | 2502.87 | 55.11 | 9.11 | 1.00 | 3367.75 | 1038.36 | 24.02 | 6997.22 | 2632.67 | 118.00 | 35.70 | 40.80 | 320.00 | 6.83 |
| later period | 102 | 3040.80 | 340.50 | 52.40 | 10.30 | 5204.00 | 373.80 | 22.00 | 9040.00 | 297.00 | 13.00 | 36.80 | 41.20 | 60.80 | 6.55 |
|  | 1 | 460.85 | 80.20 | 8.51 | 0.00 | 265.88 | 158.65 | 500.00 | 1474.00 | 330.00 | 14.00 | 21.50 | 32.90 | 76.20 | 6.00 |
|  | 102H1-1 | 2995.20 | 29.50 | 4.50 | 13.00 | 4426.50 | 396.90 | 8.50 | 7867.80 | 606.00 | 30.00 | 18.70 | 30.90 | 40.50 | 6.67 |
|  | 105 | 4174.90 | 58.10 | 20.70 | 40.00 | 5920.20 | 781.80 | 417.90 | 11380.10 | 890.00 | 42.00 | 22.80 | 33.10 | 43.20 | 6.60 |
|  | 103 | 4777.70 | 140.30 | 12.20 | 9.00 | 7090.00 | 580.30 | 336.20 | 12943.30 | 600.00 | 30.00 | 22.90 | 35.80 | 39.00 | 6.67 |
|  | 102H1-5 | 1075.50 | 14.00 | 1.20 | 18.00 | 1099.00 | 1050.60 | 16.80 | 3372.60 | 470.00 | 22.00 | 23.20 | 36.10 | 50.80 | 7.36 |
|  | 102H1-4 | 4386.00 | 104.20 | 25.50 | 7.80 | 6664.60 | 647.40 | 4.80 | 11839.30 | 550.00 | 25.00 | 20.90 | 29.80 | 45.00 | 6.72 |
|  | 105H1-2 | 7267.50 | 288.60 | 31.60 | 45.00 | 11627.60 | 470.30 | 9.60 | 19702.00 | 380.00 | 18.00 | 18.70 | 27.90 | 50.20 | 6.83 |
|  | 108H1-1 | 5742.70 | 152.30 | 25.50 | 12.00 | 8791.60 | 714.60 | 33.60 | 15467.10 | 450.00 | 20.00 | 13.10 | 25.30 | 38.40 | 6.75 |

Table 2. The water quality indicators of inlet and discharge streams in integrated regulating tank

| Item | SS | pH | DO | CODCr | BOD5 | NH3-N | TN | TOC | TDS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Unit | mg.L-1 |  | mg.L-1 | mg.L-1 | mg.L-1 | mg.L-1 | mg.L-1 | mg.L-1 | mg.L-1 |
| Inlet | 314 | 7.7 | 4.64 | 1240 | 95 | 28.33 | 39.1 | 477 | 19760 |
| Discharge | ≤10 | 6-9 | ≥5 | ≤20 | ≤4 | ≤1 | ≤10 | - | - |
| Item | TP | F- | As | Oil | Anionic surfactant | Cl- | SO42- | NO3- | Fe |
| Unit | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |
| Inlet | 1.29 | 1.65 | 0.55 | 3.12 |  | 8750 | 22.1 | 0.281 | 3.83 |
| Discharge | ≤0.2 | ≤1 | ≤0.05 | ≤0.05 | ≤0.2 | ≤250 | ≤250 | ≤10 | ≤0.3 |
| Item | Hardness | HCO3- | Ca2+ | Mg2+ | Si | B | Ba | Sr | Sb |
| Unit | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |
| Inlet | 950 | 1020 | 215 | 33.75 | 23.45 | 17.12 | 39.5 | 39.41 | 0.26 |
| Discharge | - | - | - | - | - | - | - | - | - |

Table 3. Monitored online data for CODCr, NH3-N, TN and TP in the effluent(mg.L-1)

|  | CODCr |  | NH3-N |  | TN |  | TP |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Outlet | standard | Outlet | standard | Outlet | standard | Outlet | standard |
| 2022-07-20 | 1.641 | 20 | 0.026 | 1 | 0.868 | 10 | 0.014 | 0.2 |
| 2022-07-19 | 3.036 | 20 | 0.06 | 1 | 0.628 | 10 | 0.017 | 0.2 |
| 2022-07-18 | 2.304 | 20 | 0.039 | 1 | 1.347 | 10 | 0.014 | 0.2 |
| 2022-07-17 | 6.012 | 20 | 0.176 | 1 | 0.479 | 10 | 0.012 | 0.2 |
| 2022-07-16 | 4.634 | 20 | 0.164 | 1 | 0.478 | 10 | 0.012 | 0.2 |
| 2022-07-15 | 3.117 | 20 | 0.027 | 1 | 0.337 | 10 | 0.016 | 0.2 |
| 2022-07-14 | 1.511 | 20 | 0.303 | 1 | 0.594 | 10 | 0.129 | 0.2 |
| 2022-07-13 | 1.419 | 20 | 0.014 | 1 | 0.45 | 10 | 0.023 | 0.2 |
| 2022-07-12 | 1.419 | 20 | 0.016 | 1 | 0.402 | 10 | 0.023 | 0.2 |
| 2022-07-11 | 1.419 | 20 | 0.018 | 1 | 0.277 | 10 | 0.019 | 0.2 |
| 2022-07-10 | 2.349 | 20 | 0.032 | 1 | 0.48 | 10 | 0.016 | 0.2 |
| 2022-07-09 | 1.62 | 20 | 0.017 | 1 | 1.656 | 10 | 0.011 | 0.2 |
| 2022-07-08 | 1.41 | 20 | 0.04 | 1 | 2.226 | 10 | 0.013 | 0.2 |
| 2022-07-07 | 0.742 | 20 | 0.018 | 1 | 1.108 | 10 | 0.007 | 0.2 |
| 2022-07-06 | 1.957 | 20 | 0.037 | 1 | 2.03 | 10 | 0.01 | 0.2 |
| 2022-07-05 | 1.29 | 20 | 0.043 | 1 | 2.24 | 10 | 0.01 | 0.2 |
| 2022-07-04 | 1.29 | 20 | 0.043 | 1 | 2.24 | 10 | 0.01 | 0.2 |
| 2022-07-03 | 1.636 | 20 | 0.037 | 1 | 2.49 | 10 | 0.011 | 0.2 |
| 2022-07-02 | 2.99 | 20 | 0.019 | 1 | 2.733 | 10 | 0.015 | 0.2 |
| 2022-07-01 | 3.037 | 20 | 0.034 | 1 | 2.741 | 10 | 0.013 | 0.2 |
| 2022-06-30 | 3.102 | 20 | 0.027 | 1 | 2.778 | 10 | 0.013 | 0.2 |
| 2022-06-29 | 2.022 | 20 | 0.019 | 1 | 2.377 | 10 | 0.015 | 0.2 |
| 2022-06-28 | 1.27 | 20 | 0.024 | 1 | 2.567 | 10 | 0.013 | 0.2 |
| 2022-06-27 | 1.27 | 20 | 0.024 | 1 | 2.62 | 10 | 0.01 | 0.2 |
| 2022-06-26 | 1.27 | 20 | 0.024 | 1 | 2.62 | 10 | 0.01 | 0.2 |
| 2022-06-25 | 1.27 | 20 | 0.024 | 1 | 2.62 | 10 | 0.01 | 0.2 |
| 2022-06-24 | 1.962 | 20 | 0.024 | 1 | 2.671 | 10 | 0.013 | 0.2 |
| 2022-06-23 | 4.931 | 20 | 0.037 | 1 | 2.59 | 10 | 0.013 | 0.2 |
| 2022-06-22 | 3.335 | 20 | 0.376 | 1 | 0.15 | 10 | 0.025 | 0.2 |
| 2022-06-21 | 2.9 | 20 | 0.037 | 1 | 0.09 | 10 | 0.018 | 0.2 |

Table 4. Water quality test results of each unit

|  | COD (mg/L) | NH3-N (mg/L) | TN (mg/L) | As (mg/L) | TDS (mg/L) | pH |
| --- | --- | --- | --- | --- | --- | --- |
| inlet | 1240 | 28.33 | 39.1 | 0.55 | 19760 | 7.7 |
| Oil isolation | 1787.79 | 30.32 | 114.48 | 0.64 | 21321.46 | 7.86 |
| Air flotation | 1573.25 | 30.32 | 114.48 | 0.64 | 21563.21 | 9.1 |
| De-hardening precipitation | 1573.25 | 30.32 | 114.48 | 0.64 | 21563.21 | 8.25 |
| Fenton oxidation | 892 | 36.38 | 114.48 | 0.13 | 23062.63 | 8.65 |
| Flocculation precipitation | 895.98 | 36.30 | 114.38 | 0.13 | 23026.64 | 8.65 |
| MVR evaporation | 107.36 | 30.95 | 35.8 | 0.01 | 279.97 | 8.37 |
| AO/MBR | 4.83 | 0.37 | 30.07 | 0.01 | 426.35 | 8.03 |
| RO membrane | Did not check out | Did not check out | 0.75 | Did not check out | 3.30 | 7.12 |

Table 5. Total outlet water quality and standard water quality.

| Item | pH | DO | CODMn | CODCr | BOD5 | NH3-N | TN | TP |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Unit |  | mg.L-1 | mg.L-1 | mg.L-1 | mg.L-1 | mg.L-1 | mg.L-1 | mg.L-1 |
| Outlet | 7.12 | 5.5 | <0.5 | <4 | <0.5 | <0.025 | 0.75 | 0.02 |
| standard | 6-9 | ≥5 | ≤6 | ≤20 | ≤4 | ≤1 | ≤1 | ≤0.2 |
| Item | CN- | Volatile phenol | Oil | Anionic surfactant | S2- | E. coli | SO42- | NO3- |
| Unit | mg.L-1 | mg.L-1 | mg.L-1 | mg.L-1 | mg.L-1 | mg.L-1 | mg.L-1 | mg.L-1 |
| Outlet | 0.001 | 0.005 | 0.04 | 0.089 | 0.013 | 20 | 0.398 | 0.27 |
| standard | ≤0.2 | ≤0.005 | ≤0.05 | ≤0.2 | ≤0.2 | ≤10000 | ≤250 | ≤10 |

Table 6. List of drug consumption

| Name | Unit | Quantity | Remarks |
| --- | --- | --- | --- |
| Treated water volume | m3/d | 480 |  |
| Power consumption | kw.hr/d | 22300 |  |
| Natural gas consumption | m³/d | 897 |  |
| Water consumption | m³/d | 360 | Use produce water of RO membrane |
| PAM | kg/d | 7.34 | Purchase of solids |
| PAC | kg/d | 120.33 | Purchase of solids |
| Na2CO3 | kg/d | 75.95 | Purchase of solids |
| H2O2 | kg/d | 1093.02 | Purchase of liquid （30% concentration ） |
| FeSO4 | kg/d | 893.70 | Purchase of solids |
| NaOH | kg/d | 2242.79 | Purchase of liquid （30% concentration ） |
| H2SO4 | kg/d | 81.88 | Purchase of liquid （ 30% concentration ） |
| Scale inhibitor | kg/d | 1.52 | Purchase of solids |
| NaClO | kg/d | 2.63 | Purchase of liquid （ 10% concentration ） |
| Citric acid | kg/d | 1.58 | Purchase of solids |
| NaHSO3 | kg/d | 0.37 | Purchase of solids |
| Sludge | kg/d | 2405.31 | Water content 65% |
| Crystalline salt | kg/d | 11126.11 | Water content 5% |

Table 7.  Direct operating costs

| Name | Unit | Costs（Yuan） |
| --- | --- | --- |
| Treated water volume | m³/d | 480 |
| Electric charge | Yuan /d | 13380 |
| Natural gas charge | Yuan /d | 1524.9 |
| Pharmaceutical charge | Yuan /d | 7465.19 |
| Labor charge | Yuan /d | 2000 |
| Solid waste disposal charge | Yuan /d | 3818.89 |
| Direct operating costs | Yuan /m3 | 58.73 |

The cost does not include depreciation cost, maintenance and repair cost, management cost, only direct operating cost, and varies according to the change of unit price of local consumption。