## Overview Data for models
LCA over GAC treatment | [6 empty] | Health-effects of PFAS model
Regeneration frequency required to meet 4.4 ng PEQ/L guideline | [6 empty] | Current drinking water concentrations |  |  |  |  | prospective drinking water concentrations
Based on 2024 data | time to regeneration (days) | regeneration frequency (/year) |  |  |  | Based on 2024 data | PFOA | PFNA | PFOS | PFHxS |  | PFOA | PFNA | PFOS | PFHxS
Average | 199.0634 | 1.8336 |  |  |  | Average | 5.5038 |  | 0.96877 | 1.3832 |  | 1.8973 |  | 0.28496 | 0.39594
Min | 224.7051 | 1.6244 |  |  |  | 95 % CI LL | 4.9432 |  | 0.77374 | 1.2174 | removal (avg, relative to current DW) | 65.53% |  | 70.58% | 71.38%
Max | 173.4218 | 2.1047 |  |  |  | 95 % CI UL | 6.0645 |  | 1.1638 | 1.5491
GAC amounts used in 2024
GAC density (based on 2022 data) | 376.5 | kg/m3
Volume per GAC filter | 145 | m3/filter
Number of GAC filters in stage 2 | 20
New GAC used in 2024 | 930920 | kg (per year)
% regenerated carbon in 2024 | 87.5%
Total volume of GAC filters | 2900 | m3
Total volume of new GAC entering treatment plant in 2024 | 2472.5631 | m3
renewed filters in 2024 | 17
Regeneration frequency in 2024 | 0.85261 | per year | alternative calculation based on nr. of renewed filters
Average time until regeneration in 2024 | 428.0983 | days | 429.4118 | days | ~ same result
increased regeneration frequency ('new' scenario)
Units: kg (per year) | 2024 ('old' scenario) | average | min | max
Virgin GAC | 116365 | 250250.1773 | 221693.4942 | 287251.4873
Regenerated GAC | 814555 | 1751751.2413 | 1551854.4594 | 2010760.4112
Total GAC | 930920 | 2002001.4186 | 1773547.9536 | 2298011.8986
Drinking water conc. 2024 (ng PEQ/L; recorded data) | 10.364 | *Leiduin 1 and 2 taken independently, not weighed
Calculate concentration from known stand time
Raw water concentration (ng PEQ/L) | 21.5935
stand time * 0.5 | 214.0491
m | 0.0020472
breakthrough | 43.82%
concentration in drinking water | 9.4625
difference with actual concentration | 8.699%
Check if assumption to ignore 1st stage is valid (for 2024 data):
Calculate concentration from known stand time | stage 1 | stage 2 | time in stage 1
stand time filter (days) | 556.5278 | 428.0983 | 128.4295
m | 0.0020472 | 0.0020472
breakthrough | 113.9% | 87.64%
influent | 21.5935 | Influent ng PEQ/L
after 1st stage | 21.6446 | ng PEQ/L
after 2nd stage | 9.4848 | ng PEQ/L | Very similar result
relative difference: | 8.483%
To check the calculation method, the known operational time of the filters in 2024 and the known raw water PEQ concentration in 2024 were used to calculate the drinking water PEQ concentration in 2024. The calculated drinking water concentration was sufficiently close (8.7 %) to the measured drinking water concentration in 2024.

## InfluentData
Raw water concentrations, ng/L |  | PFOA | PFNA | PFOS | PFHxS | PEQ_LB
| slope (m) of regression model | 0.0023788 |  | 0.0007122 | 0.001755 | 0.0020472 | Uncertainty analysis over PEQ concentrations
| 2024-12-02 11:01 | 7.2 | <0.5 | 4.2 | 2 | 18.8336 | slope average | 0.0020472
| 2024-11-04 13:02 | 7.6 | 0.5 | 4.5 | 2.2 | 25.2524 | standard error slope | 5.3211e-05
| 2024-10-07 13:18 | 7.8 | 0.74 | 4.4 | 2.2 | 28.1683 | standard error influent conc. (2024) | 1.2096 | tinv influent | 2.1448 | 95% CI influent | 2.5943
| 2024-09-09 11:31 | 8.3 | 0.5 | 5.1 | 2.1 | 27.6408 | standard error time to regeneration | 12.2925 | 1.6056 | 0.34569
| 2024-08-12 13:25 | 9.1 | 0.5 | 4.3 | 2.4 | 32.3169 | degrees of freedom influent conc. | 14 | in 2024
| 2024-07-16 13:32 | 10 | <0.50 | 4.4 | 2.5 | 22.7863 | degrees of freedom slope | 242
| 2024-07-15 13:28 | 8.9 | <0.50 | 3.2 | 2.3 | 19.3492 |  |  | var slope | var influent
| 2024-07-03 07:04 | 8 | <0.50 | 4.2 | 2.4 | 20.3051 | effective degrees of freedom | 20.6223 | 26.7703 | 124.3348
| 2024-06-17 11:33 | 8.1 | <0.50 | 3.3 | 2.2 | 18.1861 | t-value | 2.086
| 2024-05-21 10:47 | 8.3 | <0.50 | 3.5 | 2.2 | 18.7871 | 95% CI time to regeneration | 25.6417
| 2024-04-22 12:53 | 7 | <0.50 | 3.2 | 2.3 | 16.5027
| 2024-03-25 12:39 | 6.9 | <0.50 | 3.4 | 2.1 | 16.4771
| 2024-02-26 14:17 | 7.8 | <0.50 | 3.8 | 2.3 | 18.755
| 2024-01-29 10:47 | 7.5 | <0.50 | 4.3 | 2.4 | 19.962
| 2024-01-02 14:02 | 7.7 | <0.50 | 4.5 | 2.4 | 20.5806
[7 empty] | Removal required: | breakthrough | time to regeneration/2 | time to regeneration | regenerations per year
| AVERAGE 2024 | 8.0133 | 0.56 | 4.02 | 2.2667 | 21.5935 | 79.62% | 20.38% | 99.5317 | 199.0634 | 1.8336
| MIN 2024 | 6.9 | 0.5 | 3.2 | 2 | 16.4771 | 73.3% | 26.7% | 112.3525 | 224.7051 | 1.6244
| MAX 2024 | 10 | 0.74 | 5.1 | 2.5 | 32.3169 | 86.38% | 13.62% | 86.7109 | 173.4218 | 2.1047
breakthrough at prospective regeneration frequency: |  | 23.68% | 0% | 7.089% | 17.47% | 20.38%
prospective concentration: |  | 1.8973 | 0 | 0.28496 | 0.39594 | 4.4

## PFOA
Description | Date of sample | Component | Unit | Value | Weight | Concentration
Drinkwater Leiduin 2 | 2024-12-02 10:31 | som L-PFOA en B-PFOA, indicatief | ng/l | 4.4 | 0.3 | 4.26 | avg | 5.5038
Drinkwater Leiduin 1 | 2024-12-02 10:21 | som L-PFOA en B-PFOA, indicatief | ng/l | 4.2 | 0.7 |  | min | 4.11
Drinkwater Leiduin 2 | 2024-11-04 11:19 | som L-PFOA en B-PFOA, indicatief | ng/l | 4.7 | 0.3 | 4.56 | max | 7.11
Drinkwater Leiduin 1 | 2024-11-04 11:06 | som L-PFOA en B-PFOA, indicatief | ng/l | 4.5 | 0.7 |  | std | 0.92771
Drinkwater Leiduin 2 | 2024-10-07 10:30 | som L-PFOA en B-PFOA, indicatief | ng/l | 3.9 | 0.3 | 4.11 | standard error | 0.2573
Drinkwater Leiduin 1 | 2024-10-07 10:03 | som L-PFOA en B-PFOA, indicatief | ng/l | 4.2 | 0.7 |  | t-value | 2.1788
Drinkwater Leiduin 2 | 2024-09-09 10:02 | som L-PFOA en B-PFOA, indicatief | ng/l | 5 | 0.3 | 5.7 | margin of error | 0.56061
Drinkwater Leiduin 1 | 2024-09-09 10:01 | som L-PFOA en B-PFOA, indicatief | ng/l | 6 | 0.7 |  | lower limit | 4.9432
Drinkwater Leiduin 2 | 2024-08-12 12:58 | som L-PFOA en B-PFOA, indicatief | ng/l | 5.8 | 0.3 | 6.29 | upper limit | 6.0645
Drinkwater Leiduin 1 | 2024-08-12 11:11 | som L-PFOA en B-PFOA, indicatief | ng/l | 6.5 | 0.7
Drinkwater Leiduin 1 | 2024-07-15 10:41 | som L-PFOA en B-PFOA, indicatief | ng/l | 5 | 0.7 | 5.12
Drinkwater Leiduin 2 | 2024-07-15 10:40 | som L-PFOA en B-PFOA, indicatief | ng/l | 5.4 | 0.3
Drinkwater Leiduin 2 | 2024-06-17 10:29 | som L-PFOA en B-PFOA, indicatief | ng/l | 4.7 | 0.3 | 5.05
Drinkwater Leiduin 1 | 2024-06-17 09:25 | som L-PFOA en B-PFOA, indicatief | ng/l | 5.2 | 0.7
Drinkwater Leiduin 2 | 2024-05-21 11:25 | som L-PFOA en B-PFOA, indicatief | ng/l | 6.9 | 0.3 | 7.11
Drinkwater Leiduin 1 | 2024-05-21 06:59 | som L-PFOA en B-PFOA, indicatief | ng/l | 7.2 | 0.7
Drinkwater Leiduin 2 | 2024-04-22 12:28 | som L-PFOA en B-PFOA, indicatief | ng/l | 5.7 | 0.3 | 5.77
Drinkwater Leiduin 1 | 2024-04-22 10:09 | som L-PFOA en B-PFOA, indicatief | ng/l | 5.8 | 0.7
Drinkwater Leiduin 2 | 2024-03-25 12:14 | som L-PFOA en B-PFOA, indicatief | ng/l | 5.2 | 0.3 | 4.99
Drinkwater Leiduin 1 | 2024-03-25 09:53 | som L-PFOA en B-PFOA, indicatief | ng/l | 4.9 | 0.7
Drinkwater Leiduin 2 | 2024-02-26 11:03 | som L-PFOA en B-PFOA, indicatief | ng/l | 5.9 | 0.3 | 5.76
Drinkwater Leiduin 1 | 2024-02-26 10:25 | som L-PFOA en B-PFOA, indicatief | ng/l | 5.7 | 0.7
Drinkwater Leiduin 2 | 2024-01-29 10:57 | som L-PFOA en B-PFOA, indicatief | ng/l | 6.8 | 0.3 | 6.8
Drinkwater Leiduin 1 | 2024-01-29 07:52 | som L-PFOA en B-PFOA, indicatief | ng/l | 6.8 | 0.7
Drinkwater Leiduin 2 | 2024-01-02 12:42 | som L-PFOA en B-PFOA, indicatief | ng/l | 6.1 | 0.3 | 6.03
Drinkwater Leiduin 1 | 2024-01-02 12:17 | som L-PFOA en B-PFOA, indicatief | ng/l | 6 | 0.7

## PFNA
Description | Date of sample | Component | Unit | Value | Weight | Concentration
Drinkwater Leiduin 1 | 2024-12-02 10:21 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.7 | #VALUE! | avg | #VALUE!
Drinkwater Leiduin 2 | 2024-12-02 10:31 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.3 |  | min | #VALUE!
Drinkwater Leiduin 2 | 2024-11-04 11:19 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.3 | #VALUE! | max | #VALUE!
Drinkwater Leiduin 1 | 2024-11-04 11:06 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.7 |  | std | #VALUE!
Drinkwater Leiduin 2 | 2024-10-07 10:30 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.3 | #VALUE! | standard error | #VALUE!
Drinkwater Leiduin 1 | 2024-10-07 10:03 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.7 |  | t-value | #NUM!
Drinkwater Leiduin 2 | 2024-09-09 10:02 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.3 | #VALUE! | margin of error | #NUM!
Drinkwater Leiduin 1 | 2024-09-09 10:01 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.7 |  | lower limit | #VALUE!
Drinkwater Leiduin 2 | 2024-08-12 12:58 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.3 | #VALUE! | upper limit | #VALUE!
Drinkwater Leiduin 1 | 2024-08-12 11:11 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.7
Drinkwater Leiduin 1 | 2024-07-15 10:41 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.7 | #VALUE!
Drinkwater Leiduin 2 | 2024-07-15 10:40 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.3
Drinkwater Leiduin 2 | 2024-06-17 10:29 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.3 | #VALUE!
Drinkwater Leiduin 1 | 2024-06-17 09:25 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.7
Drinkwater Leiduin 2 | 2024-05-21 11:25 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.3 | #VALUE!
Drinkwater Leiduin 1 | 2024-05-21 06:59 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.7
Drinkwater Leiduin 2 | 2024-04-22 12:28 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.3 | #VALUE!
Drinkwater Leiduin 1 | 2024-04-22 10:09 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.7
Drinkwater Leiduin 2 | 2024-03-25 12:14 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.3 | #VALUE!
Drinkwater Leiduin 1 | 2024-03-25 09:53 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.7
Drinkwater Leiduin 2 | 2024-02-26 11:03 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.3 | #VALUE!
Drinkwater Leiduin 1 | 2024-02-26 10:25 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.7
Drinkwater Leiduin 2 | 2024-01-29 10:57 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.3 | #VALUE!
Drinkwater Leiduin 1 | 2024-01-29 07:52 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.7
Drinkwater Leiduin 2 | 2024-01-02 12:42 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.3 | #VALUE!
Drinkwater Leiduin 1 | 2024-01-02 12:17 | perfluornonaanzuur (PFNA) | ng/l | <0.50 | 0.7

## PFOS
Description | Date of sample | Component | Unit | Value | Weight | Concentration
Drinkwater Leiduin 2 | 2024-12-02 10:31 | som L-PFOS en B-PFOS, indicatief | ng/l | 0.72 | 0.3 | 0.748 | avg | 0.96877
Drinkwater Leiduin 1 | 2024-12-02 10:21 | som L-PFOS en B-PFOS, indicatief | ng/l | 0.76 | 0.7 |  | min | 0.209
Drinkwater Leiduin 2 | 2024-11-04 11:19 | som L-PFOS en B-PFOS, indicatief | ng/l | 0.76 | 0.3 | 0.879 | max | 1.64
Drinkwater Leiduin 1 | 2024-11-04 11:06 | som L-PFOS en B-PFOS, indicatief | ng/l | 0.93 | 0.7 |  | std | 0.32274
Drinkwater Leiduin 2 | 2024-10-07 10:30 | som L-PFOS en B-PFOS, indicatief | ng/l | 0.71 | 0.3 | 0.766 | standard error | 0.089512
Drinkwater Leiduin 1 | 2024-10-07 10:03 | som L-PFOS en B-PFOS, indicatief | ng/l | 0.79 | 0.7 |  | t-value | 2.1788
Drinkwater Leiduin 2 | 2024-09-09 10:02 | som L-PFOS en B-PFOS, indicatief | ng/l | 1 | 0.3 | 1.07 | margin of error | 0.19503
Drinkwater Leiduin 1 | 2024-09-09 10:01 | som L-PFOS en B-PFOS, indicatief | ng/l | 1.1 | 0.7 |  | lower limit | 0.77374
Drinkwater Leiduin 2 | 2024-08-12 12:58 | som L-PFOS en B-PFOS, indicatief | ng/l | 1.1 | 0.3 | 1.03 | upper limit | 1.1638
Drinkwater Leiduin 1 | 2024-08-12 11:11 | som L-PFOS en B-PFOS, indicatief | ng/l | 1 | 0.7
Drinkwater Leiduin 1 | 2024-07-15 10:41 | som L-PFOS en B-PFOS, indicatief | ng/l | <0.20 | 0.7 | 0.209 | * value below LOQ replaced with LOQ
Drinkwater Leiduin 2 | 2024-07-15 10:40 | som L-PFOS en B-PFOS, indicatief | ng/l | 0.23 | 0.3
Drinkwater Leiduin 2 | 2024-06-17 10:29 | som L-PFOS en B-PFOS, indicatief | ng/l | 0.94 | 0.3 | 0.982
Drinkwater Leiduin 1 | 2024-06-17 09:25 | som L-PFOS en B-PFOS, indicatief | ng/l | 1 | 0.7
Drinkwater Leiduin 2 | 2024-05-21 11:25 | som L-PFOS en B-PFOS, indicatief | ng/l | 1.5 | 0.3 | 1.64
Drinkwater Leiduin 1 | 2024-05-21 06:59 | som L-PFOS en B-PFOS, indicatief | ng/l | 1.7 | 0.7
Drinkwater Leiduin 2 | 2024-04-22 12:28 | som L-PFOS en B-PFOS, indicatief | ng/l | 1.2 | 0.3 | 1.2
Drinkwater Leiduin 1 | 2024-04-22 10:09 | som L-PFOS en B-PFOS, indicatief | ng/l | 1.2 | 0.7
Drinkwater Leiduin 2 | 2024-03-25 12:14 | som L-PFOS en B-PFOS, indicatief | ng/l | 1 | 0.3 | 1.07
Drinkwater Leiduin 1 | 2024-03-25 09:53 | som L-PFOS en B-PFOS, indicatief | ng/l | 1.1 | 0.7
Drinkwater Leiduin 2 | 2024-02-26 11:03 | som L-PFOS en B-PFOS, indicatief | ng/l | 1.1 | 0.3 | 1.03
Drinkwater Leiduin 1 | 2024-02-26 10:25 | som L-PFOS en B-PFOS, indicatief | ng/l | 1 | 0.7
Drinkwater Leiduin 2 | 2024-01-29 10:57 | som L-PFOS en B-PFOS, indicatief | ng/l | 1.2 | 0.3 | 1.13
Drinkwater Leiduin 1 | 2024-01-29 07:52 | som L-PFOS en B-PFOS, indicatief | ng/l | 1.1 | 0.7
Drinkwater Leiduin 2 | 2024-01-02 12:42 | som L-PFOS en B-PFOS, indicatief | ng/l | 0.84 | 0.3 | 0.84
Drinkwater Leiduin 1 | 2024-01-02 12:17 | som L-PFOS en B-PFOS, indicatief | ng/l | 0.84 | 0.7

## PFHxS
Description | Date of sample | Component | Unit | Value | Weight | Concentration
Drinkwater Leiduin 2 | 2024-12-02 10:31 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 0.94 | 0.3 | 0.968 | avg | 1.3832
Drinkwater Leiduin 1 | 2024-12-02 10:21 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 0.98 | 0.7 |  | min | 0.967
Drinkwater Leiduin 2 | 2024-11-04 11:19 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 0.99 | 0.3 | 1.067 | max | 1.87
Drinkwater Leiduin 1 | 2024-11-04 11:06 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.1 | 0.7 |  | std | 0.27449
Drinkwater Leiduin 2 | 2024-10-07 10:30 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 0.89 | 0.3 | 0.967 | standard error | 0.07613
Drinkwater Leiduin 1 | 2024-10-07 10:03 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1 | 0.7 |  | t-value | 2.1788
Drinkwater Leiduin 2 | 2024-09-09 10:02 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.3 | 0.3 | 1.44 | margin of error | 0.16587
Drinkwater Leiduin 1 | 2024-09-09 10:01 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.5 | 0.7 |  | lower limit | 1.2174
Drinkwater Leiduin 2 | 2024-08-12 12:58 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.6 | 0.3 | 1.6 | upper limit | 1.5491
Drinkwater Leiduin 1 | 2024-08-12 11:11 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.6 | 0.7
Drinkwater Leiduin 1 | 2024-07-15 10:41 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.3 | 0.7 | 1.3
Drinkwater Leiduin 2 | 2024-07-15 10:40 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.3 | 0.3
Drinkwater Leiduin 2 | 2024-06-17 10:29 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.1 | 0.3 | 1.24
Drinkwater Leiduin 1 | 2024-06-17 09:25 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.3 | 0.7
Drinkwater Leiduin 2 | 2024-05-21 11:25 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.8 | 0.3 | 1.87
Drinkwater Leiduin 1 | 2024-05-21 06:59 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.9 | 0.7
Drinkwater Leiduin 2 | 2024-04-22 12:28 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.5 | 0.3 | 1.5
Drinkwater Leiduin 1 | 2024-04-22 10:09 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.5 | 0.7
Drinkwater Leiduin 2 | 2024-03-25 12:14 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.4 | 0.3 | 1.47
Drinkwater Leiduin 1 | 2024-03-25 09:53 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.5 | 0.7
Drinkwater Leiduin 2 | 2024-02-26 11:03 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.5 | 0.3 | 1.43
Drinkwater Leiduin 1 | 2024-02-26 10:25 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.4 | 0.7
Drinkwater Leiduin 2 | 2024-01-29 10:57 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.8 | 0.3 | 1.73
Drinkwater Leiduin 1 | 2024-01-29 07:52 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.7 | 0.7
Drinkwater Leiduin 2 | 2024-01-02 12:42 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.4 | 0.3 | 1.4
Drinkwater Leiduin 1 | 2024-01-02 12:17 | som L-PFHxS en B-PFHxS, indicatief | ng/l | 1.4 | 0.7